Description of Minimum Clearance after ice loading

60" minimum clearance between, primary power, & the closest communications equipment.

40" minimum clearance, between secondary power & the closest communications equipment, e.g. drive hook, through bolt bracket or strand.

18'0" inches Qwest standard. 15'6" minimum clearance as measured at the center of roads, streets, commercial driveways, parking lots, & other areas subject to truck traffic.

15'6" minimum clearance where drop crosses the opposite curb line.

A 12" separation, between the Telco drop & Power drop wires, must exist at the "1st Attachment" point of connection to the building. Power entrance conduit or mast shall not be used as a support for communication drop wire. The mast however can be used as a bonding electrode for the NID.

15'6" minimum clearance as measured at the center of commercial driveways, parking lots, & other areas subject to truck traffic.

Areas used solely by pedestrians, not on horseback, & not subject to truck traffic may have a minimum clearance of 9'6".

# Text boxes

## 12 in

## 20 in

Clearances from

NON-GROUNDED Fixture

# Lamp with Non-Insulated Drip Loop

### 20 in

or

4 in

IF NOT grounded 20” Required

IF grounded 4” Required

# Lamp without Drip Loop

#### D

#### G

#### F

#### C

#### E

#### B

60”

40”

15’6”

15’6”

9’6”

18’

15’6”

.

.

### Minimum Ground Clearances after Maximum Ice Loading

12”

#### A

A

One Quarter of the pole surface MUST be clear of equipment to provide climbing space

30”

30”

30”

30”

30”

30”

30”

30”

30”

30”

B

C

D

E

###### F

##### G